## solar
|  |  | Base Case | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 9 | Case 10 | Case 11 | Case 12 | Case 13 | Case 14 | Case 15 | Case 16 | Base Case | Case 17 | Case 18
|  | Computation Message -> | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Failed | Messages | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input
~45~1~9~~-180~ | Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output
~~~8~~-5000~ | Net electric efficiency(LHV) | % | 58.9019 | 55.3824 | 55.3824 | 55.3824 | 55.6779 | 55.9372 | 56.1951 | 56.4474 | 56.6983 | 56.9542 | 57.2107 | 57.4532 | 57.704 | 57.9457 | 58.1866 | 58.4277 | 58.6682 | 58.9019 | 59.1368 | 59.3234
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL Total Investment | kUSD | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 659.6905 | 650.8161 | 650.8161 | 650.8161 | 652.6205 | 653.1941 | 653.6146 | 654.1647 | 654.7255 | 655.5389 | 656.1443 | 656.5842 | 657.0878 | 657.5736 | 658.2142 | 658.7398 | 659.1751 | 659.6905 | 660.0098 | 660.531
93¦~34~3~1~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 1.1535 | 2.1248 | 2.1248 | 2.1248 | 2.0169 | 1.9439 | 1.875 | 1.8054 | 1.7366 | 1.6623 | 1.5926 | 1.5292 | 1.4636 | 1.4007 | 1.3356 | 1.2732 | 1.2132 | 1.1535 | 1.0977 | 1.0488
93¦~83~3~1~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 1.1535 | 2.1248 | 2.1248 | 2.1248 | 2.0169 | 1.9439 | 1.875 | 1.8054 | 1.7366 | 1.6623 | 1.5926 | 1.5292 | 1.4636 | 1.4007 | 1.3356 | 1.2732 | 1.2132 | 1.1535 | 1.0977 | 1.0488
~7~118~2~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Mass flow | kg/s | 440.1215 | 4.5359e-09 | 4.5359e-09 | 4.5359e-09 | 41.5349 | 70.41 | 99.5547 | 129.3124 | 159.5628 | 191.0327 | 223.1237 | 254.0318 | 283.2431 | 314.1505 | 345.3492 | 376.8458 | 408.4426 | 440.1215 | 469.901 | 500
~7~118~3~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Enthalpy H* | kJ/kg | 1010.3528 | 1078.9569 | 1078.9569 | 1078.9569 | 987.8501 | 990.9862 | 993.6891 | 996.5198 | 999.0792 | 1002.4263 | 1005.4785 | 1006.6514 | 1006.0245 | 1006.8865 | 1007.7941 | 1008.7189 | 1009.5809 | 1010.3528 | 1010.1005 | 1011.2515
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL Annual CO2 Emission | ktonne | 1573.6803 | 1696.5111 | 1696.5111 | 1696.5111 | 1682.8391 | 1673.5674 | 1664.8165 | 1655.9801 | 1647.241 | 1637.8059 | 1628.9583 | 1620.9944 | 1612.713 | 1604.7992 | 1596.5994 | 1588.7424 | 1581.1857 | 1573.6803 | 1566.6727 | 1560.5122
|  |  | 344.6443 | 366.5467 | 366.5467 | 366.5467 | 364.6009 | 362.9107 | 361.2455 | 359.6306 | 358.0393 | 356.4308 | 354.8327 | 353.3347 | 351.7992 | 350.3317 | 348.8812 | 347.4416 | 346.0175 | 344.6443 | 343.2757 | 342.1959
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL Break-even electricity price | USD/kWhr | 0.048435 | 0.050454 | 0.050454 | 0.050454 | 0.050295 | 0.050137 | 0.049978 | 0.049826 | 0.049677 | 0.049532 | 0.049383 | 0.049241 | 0.049097 | 0.048959 | 0.048827 | 0.048695 | 0.048561 | 0.048435 | 0.048304 | 0.048207
~~~10~~-5000~ | Net fuel input(LHV) | kW | 1179914.125 | 1272010 | 1272010 | 1272010 | 1261759.125 | 1254807.625 | 1248246.125 | 1241620.875 | 1235068.5 | 1227994 | 1221360.25 | 1215389.375 | 1209179.5 | 1203246.125 | 1197098 | 1191207.125 | 1185541.125 | 1179914.125 | 1174659.75 | 1170040.75
~~~7~~-5000~ | Net power | kW | 694992.375 | 704469.1875 | 704469.1875 | 704469.1875 | 702521.375 | 701904.5 | 701453 | 700863 | 700262.8125 | 699393.875 | 698748.5 | 698280.4375 | 697745.25 | 697229.75 | 696551.1875 | 695995.375 | 695535.8125 | 694992.375 | 694656.125 | 694108
~45~3~2~~-180~ | Solar Field [45] Net heat absorbed by field | kW | 100307.0078 | 0 | 0 | 0 | 10400.9463 | 17409.8223 | 24349.8906 | 31263.0605 | 38167.3789 | 45051.7617 | 51933.7148 | 58840.543 | 65775.7969 | 72684.8906 | 79591.7656 | 86496.7344 | 93401.5547 | 100307.0078 | 107233.2188 | 113517.9297
~45~3~58~~-180~ | Solar Field [45] Field [incl. headers] efficiency (Fluid heating in field / Energy impinging focused active collector) | % | 0.63041 | / | / | / | 0.34863 | 0.43767 | 0.48971 | 0.52396 | 0.54829 | 0.56629 | 0.58026 | 0.59169 | 0.6013 | 0.60909 | 0.61566 | 0.62128 | 0.62615 | 0.63041 | 0.6343 | 0.63722
~45~1~93~~-180~ | Solar Field [45] Reflector active aperture per row | m^2 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455
~45~1~113~~-180~ | Solar Field [45] Number of operating flow paths |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
~45~1~66~~-180~ | Solar Field [45] Number of reflector rows per liquid flow path |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL Operating Hours per Year |  | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL Years for Equity Payback |  | 2.3547 | 2.5875 | 2.5875 | 2.5875 | 2.5707 | 2.5504 | 2.5299 | 2.5111 | 2.4931 | 2.4766 | 2.4594 | 2.4427 | 2.4262 | 2.4107 | 2.3967 | 2.3823 | 2.3679 | 2.3547 | 2.3406 | 2.3311
~45~10~9~~-180~ | Solar Field [45] Total estimated installed cost | USD | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984
86¦87¦68¦86¦86¦~9~4~31~~-4100~ | ST 1 Current generator power | kW | 295389.1562 | 302544.8125 | 302544.8125 | 302544.8125 | 301700.9688 | 301143.6875 | 300752.7188 | 300286.6562 | 299821.6562 | 299086.2812 | 298564.75 | 298207.4688 | 297712.75 | 297282.8438 | 296691.5625 | 296227.4062 | 295852.75 | 295389.1562 | 295082.9688 | 294775.5938
~2~112~2~~-5001~ | 112 - Feedwater outlet of Deaerator [55] -> Inlet of Splitter [56] Mass flow | kg/s | 230.8018 | 219.3183 | 219.3183 | 219.3183 | 219.539 | 220.5228 | 221.7065 | 222.9488 | 224.202 | 225.4855 | 226.7816 | 227.6009 | 228.2594 | 228.962 | 229.249 | 229.6288 | 230.0698 | 230.8018 | 231.539 | 232.3523
~2~45~2~~-5001~ | 45 - Steam outlet of HRSG 1: Evaporator (PCE) [44] - HPB1 -> Inlet of Splitter [41] Mass flow | kg/s | 84.9944 | 106.7356 | 106.7356 | 106.7356 | 104.5485 | 103.0493 | 101.5975 | 100.1147 | 98.6208 | 96.9947 | 95.4282 | 93.9663 | 92.4815 | 91.0022 | 89.4599 | 87.9598 | 86.493 | 84.9944 | 83.4906 | 82.1019
~2~103~2~~-5001~ | 103 - Steam outlet of HRSG 2: Evaporator (PCE) [93] - HPB1 -> Inlet of Splitter [90] Mass flow | kg/s | 75.0875 | 96.2205 | 96.2205 | 96.2205 | 94.1275 | 92.6906 | 91.3015 | 89.8791 | 88.4477 | 86.8799 | 85.3661 | 83.9484 | 82.3843 | 80.9576 | 79.4649 | 78.0128 | 76.5948 | 75.0875 | 73.6417 | 72.2822
~2~154~2~~-5001~ | 154 - Vapor outlet of Shell-Tube Evaporating HX (PCE) [105] -> Steam inlet of Shell-Tube Superheater (PCE) [123] Mass flow | kg/s | 42.8696 | 8.1719e-08 | 8.1719e-08 | 8.1719e-08 | 4.219 | 7.1378 | 10.0779 | 13.0308 | 16.0033 | 19.0635 | 22.1558 | 25.1311 | 28.0701 | 31.0224 | 33.984 | 36.9507 | 39.9151 | 42.8696 | 45.7845 | 48.5645
| PCI=46423 | kJ/kg
| Acoll | m^2 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733
| eta_tot,en | [-] | 0.51902 | 0.55382 | 0.54953 | 0.5453 | 0.54392 | 0.54218 | 0.54042 | 0.53859 | 0.53673 | 0.53489 | 0.53304 | 0.53108 | 0.52917 | 0.52717 | 0.52515 | 0.52313 | 0.52111 | 0.51902 | 0.51696 | 0.51451
| sol share | [-] | 0.078351 | 0 | 0 | 0 | 0.0081758 | 0.013685 | 0.019134 | 0.024561 | 0.029977 | 0.035389 | 0.040787 | 0.046177 | 0.051591 | 0.056966 | 0.062342 | 0.067697 | 0.07303 | 0.078351 | 0.083652 | 0.08844
| CO2 tax break even: | USD/tonne | 76.0824 | / | / | / | 1812.7684 | 926.452 | 605.3759 | 442.1135 | 341.9158 | 273.1762 | 223.2195 | 187.1633 | 157.8813 | 135.1 | 116.5564 | 100.8169 | 87.3331 | 76.0824 | 66.005 | 59.0914
| LCOE with break even CO2 tax | USD/kWh | 0.074656 |  |  |  | 0.71123 | 0.38636 | 0.26867 | 0.20882 | 0.1721 | 0.1469 | 0.12859 | 0.11537 | 0.10464 | 0.096289 | 0.089492 | 0.083723 | 0.07878 | 0.074656 | 0.070962 | 0.068428
| net power without sol with same fuel flow | kW | 652381.125 | 704480.75 | 704480.75 | 704480.75 | 699093.75 | 695375.5 | 691819 | 688171.5625 | 684588.8125 | 680572.1875 | 676840.5 | 673344.1875 | 669761.75 | 666347.875 | 662719.0625 | 659177.125 | 655779.9375 | 652381.125 | 649186.375 | 646345.75
| eta_sol_rad |  | 0.26779 | 0 | 0 | 0 | 0.11488 | 0.16412 | 0.19374 | 0.21269 | 0.22515 | 0.23657 | 0.24476 | 0.25073 | 0.2558 | 0.25876 | 0.26168 | 0.26443 | 0.2665 | 0.26779 | 0.26894 | 0.26681
| eta_sol_heat |  | 0.42481 | 0 | 0 | 0 | 0.32955 | 0.37502 | 0.39565 | 0.40596 | 0.41066 | 0.41778 | 0.42185 | 0.42379 | 0.42544 | 0.42487 | 0.42507 | 0.42566 | 0.42564 | 0.42481 | 0.42403 | 0.42075
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,0
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:16,2
Note on F6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:17,2
Note on G6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:15,4
Note on H6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (134,46% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 151.2 C). No heat transfer. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:45,9
Note on I6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (129,59% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:40,1
Note on J6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (125,00% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,8
Note on K6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (120,36% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:37,1
Note on L6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (115,77% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:37,2
Note on M6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (110,82% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:40,7
Note on N6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:39,5
Note on O6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:33,1
Note on P6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:29,6
Note on Q6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:29,0
Note on R6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,9
Note on S6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:26,1
Note on T6: ****************** Error Messages ******************* HRSG 1: Economiser (PCE) [47] - HPE0 heat balance error ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,3
Note on U6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,0
Note on V6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:30,8
Note on W6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,7

## hybrid evap
|  |  | Base Case | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 9 | Case 10 | Case 11 | Case 12 | Case 13 | Case 14 | Case 15 | Case 16 | Base Case | Case 17 | Case 18
[7 empty] | values set by hand | values set by hand | values set by hand
|  | Computation Message -> | Messages | Messages | Messages | Messages | Failed | Failed | Failed | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input
~45~1~9~~-180~ | Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 800 | 850 | 900
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output
~~~8~~-5000~ | Net electric efficiency(LHV) | % | 60.1001 | 55.3824 | 55.3824 | 55.3824 | 55.77 | 56.13 | 56.46 | 56.8147 | 57.1608 | 57.5035 | 57.8277 | 58.1589 | 58.5006 | 58.8385 | 59.1763 | 59.5103 | 59.8471 | 60.1001 | 60.5142 | 60.8476
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL Total Investment | kUSD | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625 | 417030.625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 605.3896 | 591.9783 | 591.9783 | 591.9783 | 594 | 594.9 | 595.6 | 596.3514 | 597.2658 | 598.1264 | 598.8018 | 599.8224 | 600.4804 | 601.3589 | 602.108 | 603.0129 | 603.7131 | 605.3896 | 605.7145 | 606.9087
93¦~34~3~1~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 0.76523 | 2.1248 | 2.1248 | 2.1248 | 1.983 | 1.875 | 1.78 | 1.6801 | 1.5794 | 1.4819 | 1.3937 | 1.2977 | 1.2079 | 1.1156 | 1.0271 | 0.93731 | 0.85213 | 0.76523 | 0.67387 | 0.58246
93¦~83~3~1~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 0.76523 | 2.1248 | 2.1248 | 2.1248 | 1.983 | 1.875 | 1.78 | 1.6801 | 1.5794 | 1.4819 | 1.3937 | 1.2977 | 1.2079 | 1.1156 | 1.0271 | 0.93731 | 0.85213 | 0.76523 | 0.67387 | 0.58246
~7~118~2~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Mass flow | kg/s | 692.0001 | 4.5359e-09 | 4.5359e-09 | 4.5359e-09 | 63.02 | 110.2 | 156.4 | 196.6064 | 242.5415 | 289.1821 | 336.6395 | 384.9446 | 434.0473 | 484.0544 | 534.9015 | 586.5169 | 638.9172 | 692.0001 | 749.9974 | 808.3701
~7~118~3~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Enthalpy H* | kJ/kg | 1093.1523 | 1092.1775 | 1092.1775 | 1092.1775 | 1086.8 | 1087.1 | 1086.3 | 1080.8557 | 1081.4977 | 1082.3422 | 1083.3492 | 1084.4478 | 1085.6068 | 1086.8245 | 1088.0602 | 1089.2814 | 1090.4781 | 1093.1523 | 1093.6743 | 1095.4659
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL Annual CO2 Emission | ktonne | 1528.7043 | 1696.5104 | 1696.5104 | 1696.5104 | 1679.023 | 1665.652 | 1654 | 1641.6147 | 1629.177 | 1617.137 | 1606.2576 | 1594.3929 | 1583.3427 | 1571.9504 | 1561.0322 | 1549.9417 | 1539.4323 | 1528.7043 | 1517.4314 | 1506.1473
|  |  | 337.7732 | 366.5465 | 366.5465 | 366.5465 | 363.9784 | 361.6841 | 359.5381 | 357.3059 | 355.1425 | 353.0258 | 351.0467 | 349.0476 | 347.0087 | 345.016 | 343.0464 | 341.1212 | 339.2016 | 337.7732 | 335.4623 | 333.6242
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL Break-even electricity price | USD/kWhr | 0.047096 | 0.049709 | 0.049709 | 0.049709 | 0.0495 | 0.0493 | 0.0491 | 0.048871 | 0.048673 | 0.048478 | 0.048293 | 0.048113 | 0.047922 | 0.04774 | 0.047557 | 0.047383 | 0.047204 | 0.047096 | 0.04687 | 0.04671
~~~10~~-5000~ | Net fuel input(LHV) | kW | 1146192.25 | 1272009.625 | 1272009.625 | 1272009.625 | 1258902 | 1248874 | 1240138 | 1230849.75 | 1221524.125 | 1212497 | 1204339.375 | 1195444.25 | 1187158.75 | 1178617.25 | 1170431 | 1162115.125 | 1154235.375 | 1146192.25 | 1137739.625 | 1129279.125
~~~7~~-5000~ | Net power | kW | 688863.125 | 704469.375 | 704469.375 | 704469.375 | 702127 | 700954 | 700205 | 699303.5 | 698232.875 | 697228.25 | 696441.875 | 695256.875 | 694495 | 693480.4375 | 692617.6875 | 691578.25 | 690776.125 | 688863.125 | 688493.75 | 687139
~45~3~2~~-180~ | Solar Field [45] Net heat absorbed by field | kW | 100432.2344 | 0 | 0 | 0 | 9546 | 16664 | 23768 | 30948.7676 | 38025.3086 | 45094.3164 | 52156.5859 | 59213.3555 | 66264.7891 | 73310.9766 | 80352.6328 | 87390.6406 | 94425.2266 | 100432.2344 | 108451.7031 | 115448.2031
~45~3~58~~-180~ | Solar Field [45] Field [incl. headers] efficiency (Fluid heating in field / Energy impinging focused active collector) | % | 0.61529 | / | / | / | 0.3093 | 0.4049 | 0.462 | 0.50136 | 0.528 | 0.54788 | 0.56328 | 0.57554 | 0.58553 | 0.5938 | 0.60078 | 0.60673 | 0.61186 | 0.61529 | 0.62007 | 0.62341
~45~1~93~~-180~ | Solar Field [45] Reflector active aperture per row | m^2 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525 | 943.9525
~45~1~113~~-180~ | Solar Field [45] Number of operating flow paths |  | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109
~45~1~66~~-180~ | Solar Field [45] Number of reflector rows per liquid flow path |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL Operating Hours per Year |  | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL Years for Equity Payback |  | 2.059 | 2.3011 | 2.3011 | 2.3011 | 2.281 | 2.259 | 2.238 | 2.2161 | 2.1967 | 2.178 | 2.1602 | 2.1443 | 2.1264 | 2.1105 | 2.0944 | 2.0799 | 2.0646 | 2.059 | 2.0387 | 2.0273
~45~10~9~~-180~ | Solar Field [45] Total estimated installed cost | USD | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824 | 137877824
86¦87¦68¦86¦86¦~9~4~31~~-4100~ | ST 1 Current generator power | kW | 289204.2188 | 302545.0312 | 302545.0312 | 302545.0312 | 301170 | 299975 | 299306 | 298373.3125 | 297365.9375 | 296419.4688 | 295702.875 | 294579.3125 | 293805.4688 | 292847.375 | 292024.0312 | 290992.75 | 290153 | 289204.2188 | 288241.7188 | 287214.375
~2~58~2~~-5001~ | 58 - Feedwater outlet of Deaerator [55] -> Inlet of Splitter [56] Mass flow | kg/s | 218.2178 | 219.3182 | 219.3182 | 219.3182 | 219.2 | 219 | 219.1 | 218.9608 | 218.9068 | 218.8583 | 218.8886 | 218.6686 | 218.5296 | 218.4417 | 218.452 | 218.2991 | 218.2895 | 218.2178 | 218.1915 | 218.1309
~2~47~2~~-5001~ | 47 - Water outlet of HRSG 1: Economiser (PCE) [46] - HPE3 -> Inlet of Splitter [110] Mass flow | kg/s | 111.0927 | 106.7356 | 106.7356 | 106.7356 | 107.1 | 107.4 | 107.7 | 107.9546 | 108.1919 | 108.4856 | 108.9386 | 109.246 | 109.6216 | 109.9976 | 110.392 | 110.6025 | 110.8696 | 111.0927 | 111.3418 | 111.5562
~2~64~2~~-5001~ | 64 - Water outlet of HRSG 2: Economiser (PCE) [95] - HPE3 -> Inlet of Splitter [112] Mass flow | kg/s | 91.841 | 96.2204 | 96.2204 | 96.2204 | 95.79 | 95.43 | 95.26 | 94.9326 | 94.7003 | 94.4352 | 94.1088 | 93.6564 | 93.2748 | 92.8984 | 92.5989 | 92.2955 | 92.0794 | 91.841 | 91.625 | 91.4044
~2~117~2~~-5001~ | 117 - Vapor outlet of Shell-Tube Evaporating HX (PCE) [105] -> Inlet of Splitter [92] Mass flow | kg/s | 82.4891 | 8.1719e-08 | 8.1719e-08 | 8.1719e-08 | 8.394 | 14.6 | 20.53 | 26.1987 | 32.0104 | 37.7934 | 43.5481 | 49.2932 | 54.7171 | 60.3643 | 65.9629 | 71.5329 | 77.0297 | 82.4891 | 88.2798 | 93.9724
PCI=46423
| Acoll | m^2 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482 | 205781.6482
eta_en,tot | eta_tot,en |  | 0.52552 | 0.55382 | 0.54938 | 0.54501 | 0.54438 | 0.54336 | 0.54213 | 0.54101 | 0.53978 | 0.53848 | 0.53699 | 0.5355 | 0.53409 | 0.53259 | 0.53107 | 0.52947 | 0.52789 | 0.52552 | 0.52451 | 0.52274
| sol share |  | 0.080563 | 0 | 0 | 0 | 0.0075257 | 0.013168 | 0.018805 | 0.024528 | 0.03019 | 0.035858 | 0.04151 | 0.047195 | 0.052867 | 0.058558 | 0.064242 | 0.06994 | 0.075621 | 0.080563 | 0.087027 | 0.09275
| CO2 tax break even: | USD/tonne | 11.3845 |  |  |  | 1063.6664 | 520.6395 | 332.681 | 227.5846 | 167.0026 | 126.4397 | 98.3547 | 76.8529 | 59.0323 | 45.1127 | 33.5646 | 24.1518 | 15.9279 | 11.3845 | 3.2649 | -1.7677
| LCOE with break even CO2 tax | USD/kWh | 0.050941 |  |  |  | 0.3001 | 0.1722 | 0.12766 | 0.10241 | 0.088045 | 0.078353 | 0.07158 | 0.066359 | 0.061967 | 0.058501 | 0.055583 | 0.053173 | 0.051031 | 0.050941 | 0.047965 | 0.046121
| net power without sol with same fuel flow | kW | 629765.125 | 704480.625 | 704480.625 | 704480.625 | 697367.375 | 691819 | 686858.5 | 681540.9375 | 676078.375 | 670756.9375 | 665958.875 | 660584.1875 | 655494.5 | 650223.875 | 645064.6875 | 640000.5 | 634959.5 | 629765.125 | 624259.875 | 618703.375
| eta_sol_rad |  | 0.35898 | 0 | 0 | 0 | 0.1542 | 0.22196 | 0.25943 | 0.28773 | 0.3076 | 0.32159 | 0.32918 | 0.33699 | 0.34459 | 0.35034 | 0.35551 | 0.35806 | 0.36166 | 0.35898 | 0.36723 | 0.36952
| eta_sol_heat |  | 0.58844 | 0 | 0 | 0 | 0.4986 | 0.54819 | 0.56153 | 0.57393 | 0.58263 | 0.58702 | 0.58445 | 0.58556 | 0.58856 | 0.59004 | 0.5918 | 0.5902 | 0.59112 | 0.58844 | 0.59228 | 0.59278
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [65] : Remark: 11 - Maximum suction flow violated. Pump (PCE) [65] : Remark: 31 - Motor is running beyond 105% of Nameplate capacity. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:30,6
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:15,7
Note on F6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:14,8
Note on G6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:15,0
Note on H6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (134,46% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 151.2 C). No heat transfer. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:43,4
Note on I6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (129,59% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:39,3
Note on J6: ***************** Fatal Error Messages ***************** Computation abnormally stopped ! THERMOFLEX may identify the problematic subroutine for you if you select to 'Write to Debug Log file' at the Options\Set Preferences...\Others input tab, and then repeat the computation.
Note on K6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (112,01% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.8 C). No heat transfer. Pump (PCE) [53] : Advisory: 22 - Present design conditions prevent proper sizing of pump. This pump cannot be switched to Engineering Design mode. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [53] : Remark: 13 - Pump nameplate head <= 0. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:37,6
Note on L6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.8 C). No heat transfer. Pump (PCE) [53] : Advisory: 22 - Present design conditions prevent proper sizing of pump. This pump cannot be switched to Engineering Design mode. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [53] : Remark: 13 - Pump nameplate head <= 0. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:36,4
Note on M6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.9 C). No heat transfer. Pump (PCE) [53] : Advisory: 22 - Present design conditions prevent proper sizing of pump. This pump cannot be switched to Engineering Design mode. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [53] : Remark: 13 - Pump nameplate head <= 0. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:34,3
Note on N6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.8 C). No heat transfer. Pump (PCE) [53] : Advisory: 22 - Present design conditions prevent proper sizing of pump. This pump cannot be switched to Engineering Design mode. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [53] : Remark: 13 - Pump nameplate head <= 0. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:35,4
Note on O6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.9 C). No heat transfer. Pump (PCE) [53] : Advisory: 22 - Present design conditions prevent proper sizing of pump. This pump cannot be switched to Engineering Design mode. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [53] : Remark: 13 - Pump nameplate head <= 0. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:38,3
Note on P6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.8 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:38,8
Note on Q6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.9 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:37,5
Note on R6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 144.8 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:29,6
Note on S6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:35,2
Note on T6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:26,4
Note on U6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [65] : Remark: 11 - Maximum suction flow violated. Pump (PCE) [65] : Remark: 31 - Motor is running beyond 105% of Nameplate capacity. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:30,6
Note on V6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [65] : Remark: 11 - Maximum suction flow violated. Pump (PCE) [65] : Remark: 31 - Motor is running beyond 105% of Nameplate capacity. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:33,1
Note on W6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145 C). No heat transfer. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** Pump (PCE) [65] : Remark: 11 - Maximum suction flow violated. Pump (PCE) [65] : Remark: 31 - Motor is running beyond 105% of Nameplate capacity. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:35,5

## no solar
|  | Base Case | Case 1
| Computation Message -> | Messages | Messages
INPUT VARIABLE DESCRIPTION | Units | Input | Input
Ambient temperature | C | 3 | 3
OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
Net electric efficiency(LHV) | % | 55.3824 | 55.3824
FINANCIAL Total Investment | kUSD | 253381.4688 | 253381.4688
FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 359.677 | 359.677
HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 2.1248 | 2.1248
HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 2.1248 | 2.1248
FINANCIAL Annual CO2 Emission | ktonne | 1696.5104 | 1696.5104
FINANCIAL Break-even electricity price | USD/kWhr | 0.046768 | 0.046768
Net fuel input(LHV) | kW | 1272009.5 | 1272009.5
Net power | kW | 704469.4375 | 704469.4375
FINANCIAL Operating Hours per Year |  | 6570 | 6570
FINANCIAL Years for Equity Payback |  | 1.2802 | 1.2802
ST 1 Current generator power | kW | 302545.2188 | 302545.2188
PCI=46423
CO2 tax: | USD/tonne | 30 | 30
LCOE | USD/kWh | 0.057765 | 0.057765

## const
Constant values with respect to DNI:
| units | Hybrid | Hybrid evap only
FINANCIAL Total Investment | kUSD | 458479.875 | 417030.625
FINANCIAL Operating Hours per Year | h/an | 6570 | 6570
Solar Field [45] Total estimated installed cost | USD | 133320984 | 137877824
Acoll | m^2 | 198905.6733 | 205781.6482
PCI | kJ/kg | 46423 | 46423
cost of the fuel | USD/GJ | 5.687 | 5.687

## Q_sol
Q_sol and sol share with respect to the DNI

## DB fuel
Duct burner fuel mass flow with respect to the DNI

## eta
Total energy efficiency with repsect to the DNI (on the left accounts for solar energy, on the right does not accont for solar energy
η_𝑡𝑜𝑡𝑒𝑛
DNI
DNI 𝑊/𝑚^2

## field eta
Solar efficiencies with respect to the DNI

## CO2
CO_2 emissions with respect to the DNI

## LCOE
LCOE with respect to the DNI

## CO2 tax
Break even CO_2 tax and corresponding LCOE with respect to the DNI

## Comp no sol
Comparison between hybrid, hybrid with solar, and no solar
| units | no solar | solar | hybrid evap only
Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 800 | 800
Net electric efficiency(LHV) | % | 55.3824 | 58.9019 | 60.1001
FINANCIAL Total Investment | kUSD | 253381.4688 | 458479.875 | 417030.625
FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 359.677 | 659.6905 | 605.3896
HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 2.1248 | 1.1535 | 0.76523
HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 2.1248 | 1.1535 | 0.76523
FINANCIAL Annual CO2 Emission | ktonne | 1696.5104 | 1573.6803 | 1528.7043
FINANCIAL Break-even electricity price | USD/kWhr | 0.046768 | 0.048435 | 0.047096
Net fuel input(LHV) | kW | 1272009.5 | 1179914.125 | 1146192.25
Net power | kW | 704469.4375 | 694992.375 | 688863.125
FINANCIAL Operating Hours per Year |  | 6570 | 6570 | 6570
FINANCIAL Years for Equity Payback |  | 1.2802 | 2.3547 | 2.059
ST 1 Current generator power | kW | 302545.2188 | 295389.1562 | 289204.2188
eta_tot,en,sol | [-] | 0.55382 | 0.51902 | 0.52552
CO2 tax break even: | USD/tonne | / | 76.0824 | 11.3845
LCOE with break even CO2 tax | USD/kWh | / | 0.074656 | 0.050941