## ELINK
|  |  | Base Case | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 9 | Case 10 | Case 11 | Case 12 | Case 13 | Case 14
|  | Computation Message -> | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Failed | Messages | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input
~45~1~4~~-180~ | Solar Field [45] Desired delivery massflow | kg/s | 440 | 88 | 132 | 176 | 220 | 264 | 308 | 352 | 396 | 440 | 484 | 528 | 572 | 616 | 660
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output
~45~3~2~~-180~ | Solar Field [45] Net heat absorbed by field | kW | 100072.6094 | 21427.0879 | 31450.5723 | 41172.1016 | 50498.6719 | 60698.3945 | 70416.5547 | 80271.2812 | 90262.2422 | 100094.8438 | 110407.9141 | 120429.7188 | 130398.5781 | 140369.5 | 150613.6406
~45~1~10~~-180~ | Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
~~~8~~-5000~ | Net electric efficiency(LHV) | % | 58.8909 | 56.1248 | 56.4785 | 56.8282 | 57.1692 | 57.5363 | 57.8722 | 58.212 | 58.5607 | 58.8924 | 59.2233 | 59.5431 | 59.8619 | 60.1772 | 60.5021
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL Total Investment | kUSD | 458775.375 | 347411.5312 | 363327.5312 | 376806.7812 | 390552.1875 | 404049.875 | 418275.5312 | 431209.3438 | 445352.3125 | 458800.5625 | 471946.8125 | 486182.7812 | 498853.8438 | 512766.5938 | 525762.5625
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 660.1735 | 494.6765 | 518.0389 | 538.0891 | 558.6243 | 578.4915 | 599.6362 | 618.963 | 640.1023 | 660.1754 | 679.9596 | 701.0048 | 719.7617 | 740.5786 | 760.2568
93¦~34~3~1~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 1.1547 | 1.9074 | 1.8074 | 1.7071 | 1.6089 | 1.5138 | 1.4228 | 1.3322 | 1.24 | 1.155 | 1.0692 | 0.99295 | 0.91883 | 0.84212 | 0.76187
93¦~83~3~1~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 1.1547 | 1.9074 | 1.8074 | 1.7071 | 1.6089 | 1.5138 | 1.4228 | 1.3322 | 1.24 | 1.155 | 1.0692 | 0.99295 | 0.91883 | 0.84211 | 0.76187
~7~118~2~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Mass flow | kg/s | 440 | 88 | 132 | 176 | 220 | 264 | 308 | 352 | 396 | 440 | 483.9999 | 527.9999 | 572 | 615.9999 | 660.0001
~7~118~3~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Enthalpy H* | kJ/kg | 1010.8532 | 994.8016 | 1000.0292 | 1004.3586 | 1008.7516 | 1008.3728 | 1009.6658 | 1010.2476 | 1010.356 | 1010.8027 | 1010.1754 | 1010.2044 | 1010.3214 | 1010.4184 | 1010.0884
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL Annual CO2 Emission | ktonne | 1573.8369 | 1668.9167 | 1656.2241 | 1643.4893 | 1631.0344 | 1619.056 | 1607.5734 | 1596.1626 | 1584.579 | 1573.8787 | 1563.0873 | 1553.5072 | 1544.188 | 1534.5552 | 1524.4907
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL Break-even electricity price | USD/kWhr | 0.048448 | 0.048005 | 0.048079 | 0.048118 | 0.048172 | 0.0482 | 0.048268 | 0.048314 | 0.048382 | 0.048447 | 0.048511 | 0.048598 | 0.048657 | 0.048749 | 0.048823
~~~10~~-5000~ | Net fuel input(LHV) | kW | 1180031.25 | 1251320.5 | 1241803.75 | 1232255.625 | 1222916.75 | 1213936 | 1205326.125 | 1196770.75 | 1188085.875 | 1180063 | 1171971.375 | 1164788.875 | 1157801.5 | 1150578.875 | 1143032.5
~~~7~~-5000~ | Net power | kW | 694931.5 | 702300.5 | 701351.75 | 700268.4375 | 699132.0625 | 698454.375 | 697548.875 | 696664.25 | 695751.75 | 694967.6875 | 694080.6875 | 693551.25 | 693082 | 692386.4375 | 691559.125
~45~3~58~~-180~ | Solar Field [45] Field [incl. headers] efficiency (Fluid heating in field / Energy impinging focused active collector) | % | 63.0344 | 63.2463 | 63.1779 | 63.1201 | 63.0609 | 63.0663 | 63.0485 | 63.0402 | 63.0392 | 63.0352 | 63.0436 | 63.0429 | 63.0417 | 63.0402 | 63.0445
~45~1~93~~-180~ | Solar Field [45] Reflector active aperture per row | m^2 | 1438.1381 | 1512.5602 | 1481.6871 | 1456.0959 | 1430.0923 | 1432.3306 | 1424.6776 | 1421.2375 | 1420.585 | 1438.4398 | 1440.3162 | 1438.5737 | 1436.5305 | 1434.8147 | 1435.8064
~45~1~113~~-180~ | Solar Field [45] Number of operating flow paths |  | 69 | 14 | 21 | 28 | 35 | 42 | 49 | 56 | 63 | 69 | 76 | 83 | 90 | 97 | 104
~45~1~66~~-180~ | Solar Field [45] Number of reflector rows per liquid flow path |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL Operating Hours per Year |  | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL Years for Equity Payback |  | 2.3576 | 1.8093 | 1.8912 | 1.9589 | 2.0279 | 2.0901 | 2.16 | 2.222 | 2.2915 | 2.3575 | 2.4224 | 2.4936 | 2.5548 | 2.6259 | 2.6916
~45~10~9~~-180~ | Solar Field [45] Total estimated installed cost | USD | 133093888 | 40578456 | 53809380 | 65050388 | 76483560 | 87741152 | 99543456 | 110296104 | 122137424 | 133115176 | 144130480 | 155912304 | 166446848 | 178108256 | 188929088
86¦87¦68¦86¦86¦~9~4~31~~-4100~ | ST 1 Current generator power | kW | 295407 | 300880.125 | 300202.4062 | 299406.2812 | 298545.125 | 298037.4688 | 297384.875 | 296738.8125 | 295974.9688 | 295442.5938 | 294740.6562 | 294447.375 | 294104.7812 | 293631.1875 | 293022.625
~2~112~2~~-5001~ | 112 - Feedwater outlet of Deaerator [55] -> Inlet of Splitter [56] Mass flow | kg/s | 230.7793 | 221.2047 | 222.923 | 224.6782 | 226.3845 | 227.6425 | 228.7688 | 229.3567 | 229.8175 | 230.7881 | 231.8585 | 233.1595 | 234.4908 | 235.7973 | 237.0923
~2~45~2~~-5001~ | 45 - Steam outlet of HRSG 1: Evaporator (PCE) [44] - HPB1 -> Inlet of Splitter [41] Mass flow | kg/s | 85.0232 | 102.2414 | 100.0985 | 97.9141 | 95.7313 | 93.5868 | 91.4732 | 89.3393 | 87.1459 | 85.0361 | 82.7274 | 80.6349 | 78.5456 | 76.4007 | 74.1641
~2~103~2~~-5001~ | 103 - Steam outlet of HRSG 2: Evaporator (PCE) [93] - HPB1 -> Inlet of Splitter [90] Mass flow | kg/s | 75.1608 | 91.9173 | 89.864 | 87.7684 | 85.662 | 83.4513 | 81.4129 | 79.3491 | 77.2278 | 75.1687 | 72.9266 | 70.8645 | 68.8317 | 66.7293 | 64.5355
~2~154~2~~-5001~ | 154 - Vapor outlet of Shell-Tube Evaporating HX (PCE) [105] -> Steam inlet of Shell-Tube Superheater (PCE) [123] Mass flow | kg/s | 42.766 | 8.7539 | 13.0179 | 17.2742 | 21.4746 | 25.8758 | 30.0665 | 34.2984 | 38.5445 | 42.7711 | 47.1617 | 51.4387 | 55.6702 | 59.934 | 64.2911
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:28,8
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (127,16% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Shell-Tube General HX (PCE) [124] : Advisory: 20 - The design procedure for this heat exchanger is set for the two shell passes and more than two tube passes. Temperature expectations you have imposed may not be attainable with this configuration. You may consider using two or more of these heat exchangers in series or forcing the design to use 'Two shell passes and two tube passes' or 'One shell pass and a single tube pass'. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:37,0 Checking Warnings: Pipe (PCE) [94]: Engineering design sizing DP overridden.
Note on F6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (120,49% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:39,7 Checking Warnings: Pipe (PCE) [94]: Engineering design sizing DP overridden.
Note on G6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (113,81% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:34,8
Note on H6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Pipe (PCE) [112] : Remark: 17 - Sizing pressure drop results in velocity below minimum allowed. Pipe sized on minimum velocity. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:36,1 Checking Warnings: Pipe (PCE) [94]: Engineering design sizing DP overridden.
Note on I6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,8 Checking Warnings: Pipe (PCE) [94]: Engineering design sizing DP overridden.
Note on J6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:28,0
Note on K6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,0
Note on L6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:33,0
Note on M6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:16,4
Note on N6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,2
Note on O6: ****************** Error Messages ******************* HRSG 2: Economiser (PCE) [96] - HPE0 heat balance error ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:24,8
Note on P6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:24,4
Note on Q6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:24,3
Note on R6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Shell-Tube General HX (PCE) [124] : Advisory: 16 - The tube-side cooling flow in HX is defined as single phase liquid and its outlet enthalpy was limited by saturation liquid. The actual shell outlet temperature is higher than the specified value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:24,2