## ELINK
|  |  | Base Case | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 9 | Case 10 | Case 11 | Case 12 | Case 13 | Case 14 | Case 15 | Case 16 | Case 17 | Case 18 | Case 19
|  | Computation Message -> | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input
91¦~34~1~3~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Desired fuel flow | kg/s | 1.1535 | 2.125 | 2.125 | 2.125 | 2.017 | 1.944 | 1.875 | 1.805 | 1.737 | 1.662 | 1.593 | 1.529 | 1.464 | 1.401 | 1.336 | 1.273 | 1.213 | 1.098 | 1.049 | 1.1535
91¦~83~1~3~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Desired fuel flow | kg/s | 1.1535 | 2.125 | 2.125 | 2.125 | 2.017 | 1.944 | 1.875 | 1.805 | 1.737 | 1.662 | 1.593 | 1.529 | 1.464 | 1.401 | 1.336 | 1.273 | 1.213 | 1.098 | 1.049 | 1.1535
~45~1~9~~-180~ | Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output
~~~7~~-5000~ | Net power | kW | 694935.125 | 704480.75 | 704480.75 | 704480.75 | 699093.75 | 695375.5 | 691819 | 688171.5625 | 684588.8125 | 680572.1875 | 676840.5 | 673344.1875 | 669761.75 | 666347.875 | 662719.0625 | 659177.125 | 655779.9375 | 649186.375 | 646345.75 | 652381.125
| correspond à |  |  | 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 850 | 900 | 800
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:01,7
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,67% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:03,1
Note on F6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,67% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:03,3
Note on G6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,67% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:03,0
Note on H6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (134,47% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 152 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:03,4
Note on I6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (129,60% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:03,2
Note on J6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (125,00% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:03,1
Note on K6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (120,33% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:03,0
Note on L6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (115,80% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,6
Note on M6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (110,80% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,3
Note on N6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,4
Note on O6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,4
Note on P6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,5
Note on Q6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,1
Note on R6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:01,9
Note on S6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,0
Note on T6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:02,0
Note on U6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:01,8
Note on V6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:01,7
Note on W6: ****************** Advisory Messages ******************* HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:01,9