## ELINK
|  |  | Base Case | Case 1 | Case 2 | Case 3 | Case 4 | Case 5 | Case 6 | Case 7 | Case 8 | Case 9 | Case 10 | Case 11 | Case 12 | Case 13 | Case 14 | Case 15 | Case 16 | Case 17 | Case 18
|  | Computation Message -> | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Messages | Failed | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input | Input
~45~1~9~~-180~ | Solar Field [45] Aperture normal direct irradiance | W/m^2 | 800 | 0 | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 850 | 900
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output | Output
~~~8~~-5000~ | Net electric efficiency(LHV) | % | 58.9019 | 55.3824 | 55.3824 | 55.3824 | 55.6779 | 55.9372 | 56.1951 | 56.4474 | 56.6983 | 56.9542 | 57.2107 | 57.4532 | 57.704 | 57.9457 | 58.1866 | 58.4277 | 58.6682 | 59.1368 | 59.3234
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL Total Investment | kUSD | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875 | 458479.875
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 659.6905 | 650.8161 | 650.8161 | 650.8161 | 652.6205 | 653.1941 | 653.6146 | 654.1647 | 654.7255 | 655.5389 | 656.1443 | 656.5842 | 657.0878 | 657.5736 | 658.2142 | 658.7398 | 659.1751 | 660.0098 | 660.531
93¦~34~3~1~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 1.1535 | 2.1248 | 2.1248 | 2.1248 | 2.0169 | 1.9439 | 1.875 | 1.8054 | 1.7366 | 1.6623 | 1.5926 | 1.5292 | 1.4636 | 1.4007 | 1.3356 | 1.2732 | 1.2132 | 1.0977 | 1.0488
93¦~83~3~1~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 1.1535 | 2.1248 | 2.1248 | 2.1248 | 2.0169 | 1.9439 | 1.875 | 1.8054 | 1.7366 | 1.6623 | 1.5926 | 1.5292 | 1.4636 | 1.4007 | 1.3356 | 1.2732 | 1.2132 | 1.0977 | 1.0488
~7~118~2~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Mass flow | kg/s | 440.1215 | 4.5359e-09 | 4.5359e-09 | 4.5359e-09 | 41.5349 | 70.41 | 99.5547 | 129.3124 | 159.5628 | 191.0327 | 223.1237 | 254.0318 | 283.2431 | 314.1505 | 345.3492 | 376.8458 | 408.4426 | 469.901 | 500
~7~118~3~~-5001~ | 118 - Discharge of Pump (PCE) [65] -> Inlet of Solar Field [45] Enthalpy H* | kJ/kg | 1010.3528 | 1078.9569 | 1078.9569 | 1078.9569 | 987.8501 | 990.9862 | 993.6891 | 996.5198 | 999.0792 | 1002.4263 | 1005.4785 | 1006.6514 | 1006.0245 | 1006.8865 | 1007.7941 | 1008.7189 | 1009.5809 | 1010.1005 | 1011.2515
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL Annual CO2 Emission | ktonne | 1573.6803 | 1696.5111 | 1696.5111 | 1696.5111 | 1682.8391 | 1673.5674 | 1664.8165 | 1655.9801 | 1647.241 | 1637.8059 | 1628.9583 | 1620.9944 | 1612.713 | 1604.7992 | 1596.5994 | 1588.7424 | 1581.1857 | 1566.6727 | 1560.5122
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL Break-even electricity price | USD/kWhr | 0.048435 | 0.050454 | 0.050454 | 0.050454 | 0.050295 | 0.050137 | 0.049978 | 0.049826 | 0.049677 | 0.049532 | 0.049383 | 0.049241 | 0.049097 | 0.048959 | 0.048827 | 0.048695 | 0.048561 | 0.048304 | 0.048207
~~~10~~-5000~ | Net fuel input(LHV) | kW | 1179914.125 | 1272010 | 1272010 | 1272010 | 1261759.125 | 1254807.625 | 1248246.125 | 1241620.875 | 1235068.5 | 1227994 | 1221360.25 | 1215389.375 | 1209179.5 | 1203246.125 | 1197098 | 1191207.125 | 1185541.125 | 1174659.75 | 1170040.75
~~~7~~-5000~ | Net power | kW | 694992.375 | 704469.1875 | 704469.1875 | 704469.1875 | 702521.375 | 701904.5 | 701453 | 700863 | 700262.8125 | 699393.875 | 698748.5 | 698280.4375 | 697745.25 | 697229.75 | 696551.1875 | 695995.375 | 695535.8125 | 694656.125 | 694108
~45~3~2~~-180~ | Solar Field [45] Net heat absorbed by field | kW | 100307.0078 | 0 | 0 | 0 | 10400.9463 | 17409.8223 | 24349.8906 | 31263.0605 | 38167.3789 | 45051.7617 | 51933.7148 | 58840.543 | 65775.7969 | 72684.8906 | 79591.7656 | 86496.7344 | 93401.5547 | 107233.2188 | 113517.9297
~45~3~58~~-180~ | Solar Field [45] Field [incl. headers] efficiency (Fluid heating in field / Energy impinging focused active collector) | % | 63.0415 | 63.0415 | 63.0415 | 63.0415 | 34.8632 | 43.7673 | 48.9714 | 52.3957 | 54.8289 | 56.6287 | 58.0259 | 59.1687 | 60.1296 | 60.9085 | 61.5659 | 62.1279 | 62.6149 | 63.4301 | 63.7217
~45~1~93~~-180~ | Solar Field [45] Reflector active aperture per row | m^2 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455 | 1441.3455
~45~1~113~~-180~ | Solar Field [45] Number of operating flow paths |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
~45~1~66~~-180~ | Solar Field [45] Number of reflector rows per liquid flow path |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL Operating Hours per Year |  | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570 | 6570
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL Years for Equity Payback |  | 2.3547 | 2.5875 | 2.5875 | 2.5875 | 2.5707 | 2.5504 | 2.5299 | 2.5111 | 2.4931 | 2.4766 | 2.4594 | 2.4427 | 2.4262 | 2.4107 | 2.3967 | 2.3823 | 2.3679 | 2.3406 | 2.3311
~45~10~9~~-180~ | Solar Field [45] Total estimated installed cost | USD | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984 | 133320984
86¦87¦68¦86¦86¦~9~4~31~~-4100~ | ST 1 Current generator power | kW | 295389.1562 | 302544.8125 | 302544.8125 | 302544.8125 | 301700.9688 | 301143.6875 | 300752.7188 | 300286.6562 | 299821.6562 | 299086.2812 | 298564.75 | 298207.4688 | 297712.75 | 297282.8438 | 296691.5625 | 296227.4062 | 295852.75 | 295082.9688 | 294775.5938
~2~112~2~~-5001~ | 112 - Feedwater outlet of Deaerator [55] -> Inlet of Splitter [56] Mass flow | kg/s | 230.8018 | 219.3183 | 219.3183 | 219.3183 | 219.539 | 220.5228 | 221.7065 | 222.9488 | 224.202 | 225.4855 | 226.7816 | 227.6009 | 228.2594 | 228.962 | 229.249 | 229.6288 | 230.0698 | 231.539 | 232.3523
~2~45~2~~-5001~ | 45 - Steam outlet of HRSG 1: Evaporator (PCE) [44] - HPB1 -> Inlet of Splitter [41] Mass flow | kg/s | 84.9944 | 106.7356 | 106.7356 | 106.7356 | 104.5485 | 103.0493 | 101.5975 | 100.1147 | 98.6208 | 96.9947 | 95.4282 | 93.9663 | 92.4815 | 91.0022 | 89.4599 | 87.9598 | 86.493 | 83.4906 | 82.1019
~2~103~2~~-5001~ | 103 - Steam outlet of HRSG 2: Evaporator (PCE) [93] - HPB1 -> Inlet of Splitter [90] Mass flow | kg/s | 75.0875 | 96.2205 | 96.2205 | 96.2205 | 94.1275 | 92.6906 | 91.3015 | 89.8791 | 88.4477 | 86.8799 | 85.3661 | 83.9484 | 82.3843 | 80.9576 | 79.4649 | 78.0128 | 76.5948 | 73.6417 | 72.2822
~2~154~2~~-5001~ | 154 - Vapor outlet of Shell-Tube Evaporating HX (PCE) [105] -> Steam inlet of Shell-Tube Superheater (PCE) [123] Mass flow | kg/s | 42.8696 | 8.1719e-08 | 8.1719e-08 | 8.1719e-08 | 4.219 | 7.1378 | 10.0779 | 13.0308 | 16.0033 | 19.0635 | 22.1558 | 25.1311 | 28.0701 | 31.0224 | 33.984 | 36.9507 | 39.9151 | 45.7845 | 48.5645
| PCI=46423 | kJ/kg
| Acoll | m^2 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733 | 198905.6733
| eta_tot,en | [-] | 0.51902 | 0.55382 | 0.54953 | 0.5453 | 0.54392 | 0.54218 | 0.54042 | 0.53859 | 0.53673 | 0.53489 | 0.53304 | 0.53108 | 0.52917 | 0.52717 | 0.52515 | 0.52313 | 0.52111 | 0.51696 | 0.51451
| sol share | [-] | 0.078351 | 0 | 0 | 0 | 0.0081758 | 0.013685 | 0.019134 | 0.024561 | 0.029977 | 0.035389 | 0.040787 | 0.046177 | 0.051591 | 0.056966 | 0.062342 | 0.067697 | 0.07303 | 0.083652 | 0.08844
| CO2 tax break even: | USD/tonne | 76.0824 | / | / | / | 1812.7684 | 926.452 | 605.3759 | 442.1135 | 341.9158 | 273.1762 | 223.2195 | 187.1633 | 157.8813 | 135.1 | 116.5564 | 100.8169 | 87.3331 | 66.005 | 59.0914
| LCOE | USD/kWh | 0.074656 | #VALUE! | #VALUE! | #VALUE! | 0.71123 | 0.38636 | 0.26867 | 0.20882 | 0.1721 | 0.1469 | 0.12859 | 0.11537 | 0.10464 | 0.096289 | 0.089492 | 0.083723 | 0.07878 | 0.070962 | 0.068428
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,0
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:16,2
Note on F6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:17,2
Note on G6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. ***************** Computation Remarks ****************** Shell-Tube Evaporating HX (PCE) [105] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube General HX (PCE) [124] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Shell-Tube Superheater (PCE) [123] : Remark: 41 - Zero tube flow into heat exchanger. Component bypassed. Solar Field [45] : Remark: 12 - Insufficient irradiance to heat fluid above supply temperature. Field shutdown. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:15,4
Note on H6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (134,46% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 151.2 C). No heat transfer. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:45,9
Note on I6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (129,59% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:40,1
Note on J6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (125,00% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,8
Note on K6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (120,36% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:37,1
Note on L6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (115,77% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:37,2
Note on M6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (110,82% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:40,7
Note on N6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:39,5
Note on O6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:33,1
Note on P6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:29,6
Note on Q6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:29,0
Note on R6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,9
Note on S6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:26,1
Note on T6: ****************** Error Messages ******************* HRSG 1: Economiser (PCE) [47] - HPE0 heat balance error ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:27,3
Note on U6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:30,8
Note on V6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Evaporator (PCE) [49] - LPB : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. Pump (PCE) [65] : Advisory: 1 - Pump is incapable of developing required head at current flow. Pump is running above characteristic curve. You should redesign this pump with higher head margin. Solar Field [45] : Advisory: 16 - Tube wall stress exceeds maximum allowed. Review tube wall thickness and tube material selection. ***************** Computation Remarks ****************** Deaerator [55] : Remark: 14 - Steam is vented to maintain the DA maximum pressure. PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. Computation time = 00:00:32,7

## Sheet3
|  | Base Case | Case 1
| Computation Message -> | Messages | Messages
INPUT VARIABLE DESCRIPTION | Units | Input | Input
Ambient temperature | C | 3 | 3
OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
Net electric efficiency(LHV) | % | 55.3824 | 55.3824
FINANCIAL Total Investment | kUSD | 253381.4688 | 253381.4688
FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 359.677 | 359.677
HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 2.1248 | 2.1248
HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 2.1248 | 2.1248
FINANCIAL Annual CO2 Emission | ktonne | 1696.5104 | 1696.5104
FINANCIAL Break-even electricity price | USD/kWhr | 0.046768 | 0.046768
Net fuel input(LHV) | kW | 1272009.5 | 1272009.5
Net power | kW | 704469.4375 | 704469.4375
FINANCIAL Operating Hours per Year |  | 6570 | 6570
FINANCIAL Years for Equity Payback |  | 1.2802 | 1.2802
ST 1 Current generator power | kW | 302545.2188 | 302545.2188
PCI=46423
CO2 tax: | USD/tonne | 30 | 30
LCOE | USD/kWh | 0.057765 | 0.057765