## ELINK
|  |  | Base Case | Case 1
|  | Computation Message -> | Messages | Messages
| INPUT VARIABLE DESCRIPTION | Units | Input | Input
~~1~2~~-1000~ | Ambient temperature | C | 3 | 3
| OUTPUT VARIABLE DESCRIPTION | Units | Output | Output
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~25~~~-8000~ | FINANCIAL Total Investment | kUSD | 253381.4688 | 253381.4688
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~4~~~-8000~ | FINANCIAL Specific Investment (Estimated plant specific cost) | USD/kW | 359.677 | 359.677
93¦~34~3~1~~-99~ | HRSG 1: Duct Burner - Horizontal HRSG [34] Fuel flow | kg/s | 2.1248 | 2.1248
93¦~83~3~1~~-99~ | HRSG 2: Duct Burner - Horizontal HRSG [83] Fuel flow | kg/s | 2.1248 | 2.1248
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~19~~~-8000~ | FINANCIAL Annual CO2 Emission | ktonne | 1696.5104 | 1696.5104
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~11~~~-8000~ | FINANCIAL Break-even electricity price | USD/kWhr | 0.046768 | 0.046768
~~~10~~-5000~ | Net fuel input(LHV) | kW | 1272009.5 | 1272009.5
~~~7~~-5000~ | Net power | kW | 704469.4375 | 704469.4375
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~2~22~~~-8000~ | FINANCIAL Operating Hours per Year |  | 6570 | 6570
73¦76¦81¦68¦81¦70¦76¦68¦79¦85¦72¦83¦~3~7~~~-8000~ | FINANCIAL Years for Equity Payback |  | 1.2802 | 1.2802
86¦87¦68¦86¦86¦~9~4~31~~-4100~ | ST 1 Current generator power | kW | 302545.2188 | 302545.2188
PCI=46423
| CO2 tax: | USD/tonne | 30 | 30
| LCOE | USD/kWh | 0.057765 | 0.057765
Note on D6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:13,4
Note on E6: ****************** Advisory Messages ******************* HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 6 - Specified combustor exit temperature or fuel flow input has been ignored because fuel flow has been set by the network. HRSG 1: Duct Burner - Horizontal HRSG [34] : Advisory: 8 - Duct burner running at high load (141,65% of nameplate rating). HRSG 1: Evaporator (PCE) [44] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [93] - HPB1 : Advisory: 26 - Required drum pressure > maximum. Drum pressure cut off at maximum. Steam production exceeds desired value. HRSG 2: Evaporator (PCE) [98] - LPB : Advisory: 2 - Water/steam saturation temperature ( 151.8 C) too close to gas inlet temperature ( 145.5 C). No heat transfer. HRSG 2: Advisory: 5 - Duct widths for Heat exchangers, SCR/CO cats, and Duct Burners do not match within 25%. No assembly calculation. ***************** Computation Remarks ****************** PEACE: Remark: 1 - Comprehensive PEACE Outputs are not available because one or more components in the plant assembly is in Thermodynamic Design mode. HRSG 2: Remark: 30 - HRSG has not been thermally computed. No assembly thermal output available. Computation time = 00:00:13,4